# Study OF high-performance oil dampers for seismically isolated structures to counter extremely strong earthquake ground motion

DOI 10.37153/2686-7974-2019-16-964-972

Nobuyuki OGINO, Masaru KIKUCHI, Masanari OKAMOTO

# ABSTRACT

In recent years, there has been various research and development in Japan regarding seismic isolation structures for earthquakes and inland earthquakes that produce excessive ground motion, including long period earthquakes. The high-performance oil damper we are currently developing is designed to prevent collision with retaining walls by controlling displacements taking place under seismic large-amplitudes earth motion, which we consider is able to be effective in newly constructed base-isolated buildings and existing base-isolated buildings.

This report describes, as summarized below, high-performance oil dampers, experimental results with a prototype machine and results of examination by time hysteresis response analysis. As a result, it was confirmed that this oil damper is capable of controlling displacements within the design range, without impairing seismic effects, for both newly constructed base-isolated buildings and existing base-isolated buildings.

Keywords: Oil damper, Long period earthquake ground motion, Inland earthquake, Displacement suppression，Seismic isolation structures，Variable resistance force

# 1. INTRODUCTION

In Japan, various research and development (on topics including prevention of collision to retaining walls, impact damping devices, fail-safe methods, and response displacement control) have been conducted in recent years concerning seismically base-isolated structures which are designed to resist when exposed to long period earthquake motions and inland epicentral earthquakes. Generally, as a means of limiting escalation of displacement of the isolation layer in seismic waves exceeding design values of seismic action, using more dampers is a potential solution to control displacement. In this case, however, it is likely that the seismic isolation effect may be reduced at standard seismic motion levels which are used for design in Japan. To cope with this problem, we are now developing a high-performance oil damper (velocity-dependent, multi-staged oil damper) which is designed to achieve a seismic isolation effect in the design range, but when faced with extreme seismic motions also, to control isolation layer displacement so that the structure is prevented from colliding with retaining walls. We consider that this new oil damper may be used effectively in both newly constructed base-isolated buildings and existing base-isolated buildings to improve their isolation performance further.

This paper summarizes a high-performance oil damper, test findings of prototype oil dampers and reviews results from time hysteresis response analysis.

2. SUMMARY OF OIL DAMPERS

Generally, there are two kinds of oil dampers as shown in Figure1, velocity-dependent linear type and binary type.

The oil damper developed for this project, making full use of merits of the functional mechanism (the design of a valve only) of a conventional oil damper, does not need drastic remodeling, while enabling multi-staged velocity shifting. As shown in Figure2, the damper thus designed has a variable range of damping force characteristics, so that the damper produces a small attenuation to seismic force in the design range and a high attenuation in the range of motions of high amplitudes (high velocity).

In addition, the damper is able to select characteristic A or characteristic B, i.e. the upper limit and lower limit in the remodeled oil damper for an existing base-isolated building.

Characteristic A stands for a base-isolated structure with small clearance and characteristic B with large clearance.

F＝C2Vα,α=2.0

F＝C1V

60.0cm/s

38.0cm/s

F＝C2Vα,α=2.0

F＝C1V

60.0cm/s

38.0cm/s

Figure 1. Characteristics of damping force for conventional oil dampers

Figure 1. Characteristics of damping force for conventional oil dampers

Figure 2. Characteristics of damping force for high performance oil dampers

Figure 2. Characteristics of damping force for high performance oil dampers

Figure3 shows the structure of a high-performance oil damper. The oil damper consists of an inner tube, outer tube, piston rod, piston, damping valve and hydraulic oil.

The piston rod is connected with the piston, and the yellow parts (chambers A and B) in the inner tube in the diagram are filled hermetically with hydraulic oil. Damping valves (pressure regulating valve and relief valve) are built in the piston and cylinder on the bottom side to generate damping force according to a given velocity. The structure of the oil damper is the same as of a standard oil damper. Considering that it is technically difficult to make the damping coefficient higher at a given velocity, we have developed and used dedicated valves which are most suitably adapted to this damper.

Relief valve (expansion)

Relief valve (expansion)

Outer tube

Outer tube

Regulation valve(expansion)

Regulation valve(expansion)

Cylinder on bottom side

Cylinder on bottom side

Piston

Piston

Piston rod

Piston rod

Relief valve (compression)

Relief valve (compression)

Regulation valve (BTM)

Regulation valve (BTM)

Regulation valve (compression)

Regulation valve (compression)

Relief valve (BTM)

Relief valve (BTM)

Tank

Tank

Chamber A

Chamber A

Inner tube

Inner tube

Check valve

Check valve

Chamber B

Chamber B

Figure 3. Diagram of a high performance seismic isolation oil damper

規制部材

スプリング

調圧弁

ハウジン

規制部材

スプリング

調圧弁

ハウジン

3. PERFORMACE TEST OF A TEST OIL DAMPER

## 3.1 Performance test of a test oil damper

In order to understand the damping characteristics of a high-performance seismic isolation oil damper, we developed a full-sized prototype damper (characteristic B, maximum damping force 1200 KN, max. velocity 150 cm/s), and conducted a test to confirm performance. We hereunder report the test findings. The prototype oil damper used, a 2000 KN damper, has the following specifications: maximum amplitude +/-500 mm, dynamic maximum excitation force 1000 KN/150 cm/s, 2000 KN/50 cm/s or greater)

## 3.2 Summary of the prototype oil damper

The high-performance oil damper is provided with almost the same mechanism as an existing oil damper, except for the valves which are specially designed to meet the requirements of the project damper, so the valve in question features additional components which are not provided on a standard valve, capable of changing the properties of movement during the mid-course of valve stroke.

With this configuration being applied for the primary damping range, it is possible to actually achieve the damping properties as shown in Figure2.

The structural base of the oil damper currently in development is that of the bilinear type 1000 KN of a conventional standard damper. Table 1 shows the specifications of the new damper in comparison with the conventional standard damper. The test sample and the details of experiment are shown in Figure 4.

Table 1. Comparison of specifications between prototype damper and standard damper

| Item | Symbol | Unit | Current standard | Prototype damper |
| --- | --- | --- | --- | --- |
| Primary damping coefficient | C1 | kN/(cm/s) | 25 | 6.67 |
|  | C1’ | kN/(cm/s)2 | － | 0.11 |
| Secondary damping coefficient | C2 | kN/(cm/s) | 1.695 | 2.0 |
| Shifting load | Fc | kN | － | 400 |
| Shifting velocity | Vc | Cm/s | － | 60 |
| Relief load | Fr | kN | 800 | 1100 |
| Relief velocity | Vr | cm/s | 32 | 100 |
| Maximum load | F max | kN | 1000 | 1200 |
| Maximum velocity | Vmax | cm/s | 150 | 150 |

φ120

φ120

φ406

φ406

Figure 4. Prototype damper and test set up

## 3.3 Description of experiment

The experiment was conducted for the following items. Excitation conditions are shown in Tables 2 and 3.

(1)  Experiment confirming damping loads

This experiment is designed to establish a damping force-speed relationship (F-V characteristic) as planned, by applying sinusoidal wave excitation.

(2)  Experiment of characteristic-shifting

This experiment is intended to confirm shifting velocity as well as change before and after the moment of velocity shifting.

(3)  Experiment confirming frequency-dependency

This experiment is to confirm the frequency-dependency, through a test at the same velocity with several frequencies.

Table 2. Table of experimental excitation conditions (primary damping range)

Table 3.  Table of experimental excitation conditions (Secondary damping range)

## 3.4 Experimental findings

Figure 5 shows load-displacement relationships per velocity, and Figure 6 plots lines when the experimental maximum load is taken as F-V characteristic; in the graph, the upper portion is on the compression side and the lower portion on the tensile side. Hysteresis characteristics take a shape which is assumed according to velocity. There is a dead zone at the time of expansion-compression shifting, but it is possible to remove this zone by adjusting the balance of the built-in valve.

:0.25Hz

:0.5Hz

:0.8Hz

:1.0Hz

:0.25Hz

:0.5Hz

:0.8Hz

:1.0Hz

Figure  5. Load-displacement relationship (0.5Hz)                            Figure 6. F-V characteristics

(1) Experiment confirming damping load and confirmation of characteristics shifting

In the primary damping range, it is observed that at the low velocities of 20 cm/s and 40 cm/s, the test results deviate slightly from the expected value of +-10%. In other ranges, they are included in the zone of +/-10%. With regard to shifting of velocity from low to middle and high, reaction behavior varies as expected.

(2) Frequency-dependency test

In the ranges of C1 and C2, there is no frequency dependency. Even in the range of C1’ where the damping coefficient is increased (steep slope), the frequency dependency is small.

4. TIME HYSTERESIS RESPONSE ANALYSIS

High-damping rubber bearing：1100 dia.（X0.6R）

Shear modulus：0.620 N/mm2

Total thickness of rubber layer：200 mm

Numbers of bases: 14s

High-damping rubber bearing：1100 dia.（X0.6R）

Shear modulus：0.620 N/mm2

Total thickness of rubber layer：200 mm

Numbers of bases: 14s

4.1 Subject building

The subject building is a base-isolated RC structure of 15 stories, with high damping rubber bearings at the base. The total weight and natural period of the building are respectively 123,186 KN and 4.09 s (40 cm) and the yield shearing coefficient of the isolation layer is as =0.03.

Figure 7 shows a diagram for the subject building.

Figure 7. Subject building (RC 15/0)

4.2 Input seismic motion

The following data was used as seismic waves to be studied for this research. There were 7 kinds of waves in total, 4 seismic waves from the Osaka area and Chubu area (OA1, CH1, OSKH02 and AIC003) on the assumed incidence of extreme earthquakes taken along the Nankai Trough, 2 seismic waves as an epicentral earthquake in land, representing the incidence in the Uemachi fault zone (UMTA4B2EW1) and Kumamoto earthquake (2016/416) :KMM004EW), and 1 wave as an standard seismic motion level.

The seismic waves used are listed in Table 1 and pseudo velocity response spectrums in Figure8.

Table  4. List of seismic waves

Figure 8.  Pseudo response spectrums

4.3 Analysis model and cases studied

The analysis model used is a single column row, multi-degree-freedom model where the upper structure is designed to be linear to identify the effects of a high-performance oil damper, while the high-damping rubber bearing (type X06R) is a Kikuchi-Aiken model which is capable of taking account of limit deformation. The oil damper is a Maxwell type model with improved software able to reproduce F-V characteristics a high-performance model possesses.

The damping of the upper structure is 2% to the foundation with no dampers. Seismic response is analyzed in the X direction. Various case studies are shown in Table 5.

CASE-0 is an standard model ; CASE-1A and CASE-1B consists of CASE-0 model + 10 units of oil damper with characteristic A, and CASE-1B of CASE-0 model + 10 units of oil damper with characteristic B.

In CASE-1C, 10 conventional bilinear oil dampers are respectively compared with a high-performance oil damper for the study of performance.

Table 5. Various study cases

4.4 Analysis results

The maximum response distribution for each input seismic motion are indicated in Figures 9 to11. Figures 12 and 13 show the maximum response velocities and displacement time-hysteresis waveforms at the level of the seismic isolation layer, and the hysteresis loops for high damping rubber bearing and the oil damper in CASE 1B are shown Figures14 and 15.  Figure16 shows accumulated absorption energy amounts.

The standard model (CASE-0) shows a large acceleration response was produced under a hardening effect which results from a large deformation exceeding γ = 400% in the seismic isolation layer at the time of an active fault earthquake.

Under this phenomenon, both characteristics A and B of oil dampers (CASE-1A and CASE-1B) demonstrate a remarkable reduction effect in terms of response acceleration, response displacement and response layer shearing force coefficient.

As shown in Figure 11, there is no sign of increase in acceleration velocity response at the standard input seismic motion level for design (AWL2), and CASE-1A and CASE-1B demonstrate a larger seismic damping effect than the existing old damper (CASE-1C). Observing the fact that characteristic B is able to decrease seismic layer displacement by approximately a maximum of 10% than Characteristic B, it can be said that this characteristic B is able to be used effectively for the existing base-isolated structure not having sufficient isolation capacity. Since response displacement (clearance) of the seismic layer and the response of the upper structure is in a “trade-off” relationship,” it is necessary to take a maximum displacement in order to gain an effective seismic isolation.

The maximum response velocity of the seismic isolation layer is very large at the standard model, 210 cm/s in max., but installing these oil dampers makes it possible to reduce the velocity to approximately 130 cm/s, lower than the velocity limit of 150 cm/s for oil dampers.

The temperature increase of oil dampers which is calculated from accumulated absorption energy in Figure 16 is 9.1oC (surface temperature 29.1oC: AI003), is less than the temperature limit of 80o C.

Figure 9.  Maximum response distribution（CASE-0,CASE-1A,1B）【OSKH02・OS1・CH1・AIC003】

Figure 10.  Maximum response distribution（CASE-0,CASE-1A,1B）【UMTA4-B2EW1・KMM004EW】

Figure 11.  Maximum response distribution（CASE-1A,1B,1C）【UMTA4-B2EW1・AWL2】

93.93cm

56.68cm

93.93cm

56.68cm

Figure 12.  Maximum response velocity of the seismic isolation layer

Figure 13.  Time hysteresis waveforms for displacement of the seismic isolation layer（KMM004EW）

Figure 14.  Hysteresis characteristics of seismic device（CASE-1B：AIC003）

Figure 15.  Hysteresis characteristics of seismic device（CASE-1B：KMM004EW）

Figure 16.  Accumulated absorption energy amount（CASE-1B：AIC003）

5. CONCLUSIONS

As a means of controlling vibration of buildings due to extreme ground motions, we have developed high-performance oil dampers, and conducted a test to validate performance for analysis and reviewed test findings. As a result, these dampers are confirmed to be able to control displacement of a building without impairing seismic isolation effects within the design range, when they are installed in a newly-constructed base-isolated building or existing base-isolated building.

# 6. References

Ogino, N., (2017)  Response Displacement Suppression Technology and Cases Considered for Extreme Ground Motion,

AIJ Symposium of “Approaches on Seismic Isolation Technologies for the Solution against Huge Earthquakes purpose”:53-62.

Ogino N., Tsuyuki Y., Iguchi T., Nakahara M., Yamazaki H., (2016) Development of Extreme Ground Motions measures for the oil damper (Part.1 Verification of the basic characteristics and effects), AIJ Journal of Technology and Design, Architectural Institute of Japan:409-410.

Nakahara M., Ogino N., Kitagawa M., (2017) Development of Extreme Ground Motions measures for the oil damper (Part.2 prototype production and performance verification test), AIJ Journal of Technology and Design, Architectural Institute of Japan:995-996.

Ogino N., Kitagawa M., Yamaguchi Y., Nakahara M., (2017) Development of Extreme Ground Motions measures for the oil damper (Part.3 Time history response analysis), AIJ Journal of Technology and Design, Architectural Institute of Japan:997-998.

Ishihara S., Nakahara M., (2018)  Development of Tri-linear type oil damper, KYB Technical report  Vol.57:45-49.

Kikuchi M., Aiken I. D. (1997) An analytical hysteresis model for elastomeric isolation bearings. Earthquake Engineering and Structural Dynamics, (26): 215-231.

Kikuchi, M., Ishii K. Advanced hysteresis model of high-damping rubber bearings for seismic isolation. Proceedings of the 7-th Structural Engineers World Congress, 24-26 April 2019, Istanbul, Turkey.

KUMAGAIGUMI Co., Ltd., Japan, Tokyo,  nogino@ku.kumagaigumi.co.jp

Hokkaido University, Japan, Hokkaido, mkiku@eng.hokudai.ac.jp

Kayaba System Machinery Co., Ltd, Japan, Mie, okamoto-mas@kyb.co.jp